## Alternatives
AltID | PV_R16_kW | PV_R17_kW | WT_R16_kW | BESS_R4_P_kW | BESS_R4_E_kWh | MT_R15_Pmax_kW | FC_R18_kW | Notes | PV_inv_kVA_factor | WT_inv_kVA_factor | BESS_inv_kVA_factor | Inverter_PF_mode | BESS_policy_ID | MT_policy_ID | FC_policy_ID
A0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Baseline (no DER) | 1.1 | 1.1 | 1.1 | unity_pf
A1 | 10 | 3 | 0 | 0 | 0 | 30 | 0 | PV + dispatchable MT | 1.1 | 1.1 | 1.1 | unity_pf |  | D-MT-LF
A2 | 10 | 3 | 10 | 0 | 0 | 30 | 0 | PV+WT + MT | 1.1 | 1.1 | 1.1 | unity_pf |  | D-MT-LF
A3 | 10 | 3 | 10 | 15 | 30 | 30 | 0 | Add small BESS (2h) | 1.1 | 1.1 | 1.1 | unity_pf | D-BESS-1 | D-MT-LF
A4 | 10 | 3 | 10 | 30 | 60 | 30 | 0 | Mid BESS (2h) | 1.1 | 1.1 | 1.1 | unity_pf | D-BESS-1 | D-MT-LF
A5 | 10 | 3 | 10 | 30 | 90 | 30 | 0 | BESS (3h) | 1.1 | 1.1 | 1.1 | unity_pf | D-BESS-1 | D-MT-LF
A6 | 15 | 5 | 10 | 30 | 60 | 30 | 0 | Higher PV + BESS | 1.1 | 1.1 | 1.1 | unity_pf | D-BESS-1 | D-MT-LF
A7 | 20 | 6 | 10 | 30 | 60 | 30 | 0 | High PV penetration + BESS | 1.1 | 1.1 | 1.1 | unity_pf | D-BESS-1 | D-MT-LF
A8 | 15 | 5 | 15 | 30 | 90 | 30 | 0 | Higher wind + 3h BESS | 1.1 | 1.1 | 1.1 | unity_pf | D-BESS-1 | D-MT-LF
A9 | 10 | 3 | 5 | 30 | 60 | 30 | 0 | Low wind scenario architecture | 1.1 | 1.1 | 1.1 | unity_pf | D-BESS-1 | D-MT-LF
A10 | 10 | 3 | 10 | 15 | 60 | 30 | 0 | 4h BESS (same P, higher E) | 1.1 | 1.1 | 1.1 | unity_pf | D-BESS-1 | D-MT-LF
A11 | 10 | 3 | 10 | 30 | 120 | 30 | 0 | 4h BESS (higher P and E) | 1.1 | 1.1 | 1.1 | unity_pf | D-BESS-1 | D-MT-LF
A12 | 10 | 3 | 10 | 30 | 60 | 30 | 10 | Add fuel cell (hybrid dispatchable) | 1.1 | 1.1 | 1.1 | unity_pf | D-BESS-1 | D-MT-LF | D-FC-BASE
A13 | 15 | 5 | 10 | 30 | 90 | 30 | 10 | PV+FC+3h BESS (high reliability) | 1.1 | 1.1 | 1.1 | unity_pf | D-BESS-1 | D-MT-LF | D-FC-BASE
A14 | 20 | 6 | 15 | 30 | 120 | 30 | 10 | High DER upper-bound case | 1.1 | 1.1 | 1.1 | unity_pf | D-BESS-1 | D-MT-LF | D-FC-BASE

## Derived_Inverters
AltID | PV_R16_kW | PV_R17_kW | WT_R16_kW | BESS_R4_P_kW | PV_inv_kVA_factor | WT_inv_kVA_factor | BESS_inv_kVA_factor | PV_R16_Sinv_kVA | PV_R17_Sinv_kVA | WT_R16_Sinv_kVA | BESS_R4_Sinv_kVA
A0 | 0 | 0 | 0 | 0 | 1.1 | 1.1 | 1.1 | 0 | 0 | 0 | 0
A1 | 10 | 3 | 0 | 0 | 1.1 | 1.1 | 1.1 | 11 | 3.3 | 0 | 0
A2 | 10 | 3 | 10 | 0 | 1.1 | 1.1 | 1.1 | 11 | 3.3 | 11 | 0
A3 | 10 | 3 | 10 | 15 | 1.1 | 1.1 | 1.1 | 11 | 3.3 | 11 | 16.5
A4 | 10 | 3 | 10 | 30 | 1.1 | 1.1 | 1.1 | 11 | 3.3 | 11 | 33
A5 | 10 | 3 | 10 | 30 | 1.1 | 1.1 | 1.1 | 11 | 3.3 | 11 | 33
A6 | 15 | 5 | 10 | 30 | 1.1 | 1.1 | 1.1 | 16.5 | 5.5 | 11 | 33
A7 | 20 | 6 | 10 | 30 | 1.1 | 1.1 | 1.1 | 22 | 6.6 | 11 | 33
A8 | 15 | 5 | 15 | 30 | 1.1 | 1.1 | 1.1 | 16.5 | 5.5 | 16.5 | 33
A9 | 10 | 3 | 5 | 30 | 1.1 | 1.1 | 1.1 | 11 | 3.3 | 5.5 | 33
A10 | 10 | 3 | 10 | 15 | 1.1 | 1.1 | 1.1 | 11 | 3.3 | 11 | 16.5
A11 | 10 | 3 | 10 | 30 | 1.1 | 1.1 | 1.1 | 11 | 3.3 | 11 | 33
A12 | 10 | 3 | 10 | 30 | 1.1 | 1.1 | 1.1 | 11 | 3.3 | 11 | 33
A13 | 15 | 5 | 10 | 30 | 1.1 | 1.1 | 1.1 | 16.5 | 5.5 | 11 | 33
A14 | 20 | 6 | 15 | 30 | 1.1 | 1.1 | 1.1 | 22 | 6.6 | 16.5 | 33

## Dispatch_Policies
Policy_ID | Description | Equation | Notes/Constraints
D-BESS-1 | Grid-connected; charge on renewable surplus, discharge during peak/net-demand | SoC_{t+1}=SoC_t + η_ch*P_ch*Δt/E - (P_dis*Δt)/(η_dis*E) | Limits: SoCmin/SoCmax, P_ch<=Pmax, P_dis<=Pmax; forbid simultaneous ch/dis
D-MT-LF | Load-following AFTER PV+BESS. Supplies residual demand within limits | P_MT(t)=clip(P_load - P_PV - P_WT - P_BESS, Pmin, Pmax) with optional OFF state | Use Pmax=30 kW; recommend Pmin=0.3*Pmax when ON; ramp optional
D-FC-BASE | Fuel cell constant or mild load-following (set in code as base-load support) | Option 1: P_FC = const <= Pmax. Option 2: clip(residual,0,Pmax) | Use Pmax=10 kW in baseline; can extend with efficiency curve

## Global_Params
Parameter | Value
Time step Δt | 1 hour
Slack bus | R1
PV buses | R16 and R17
Wind bus | R16
BESS bus | R4
Microturbine bus | R15
Fuel cell bus | R18
PV model | Plan-B: P = P_STC*(G/G_STC)*fT, with NOCT Tcell
G_STC | 1000 W/m^2
NOCT | 45 °C
Ambient temperature Tamb | 25 °C (assumed; replace if available)
PV temp coefficient γ | -0.003 /°C
Inverter kVA margin | S_inv = 1.10 * P_rated
Inverter Q control | Unity PF (Q=0) in Stage-1; Volt-Var optional later
BESS η_ch | 0.95
BESS η_dis | 0.95
BESS SoC min | 0.20
BESS SoC max | 0.90
BESS initial SoC | 0.50
BESS timestep constraint | No simultaneous charge/discharge
MT Pmin fraction (when ON) | 0.30 of Pmax (recommended)